## Version control
Version | Issue date | Comments/changes
2.8 | 2020-08-01 | First issue.
2.9 | 2021-01-01 | Intermediate draft.
3 | 2021-03-01 | Form AR1 deleted. This is supplied directly by the Environment Agency when requesting the annual return or on request. Form CON2 corrected as follows: Annual mean: Original footnote (g) deleted; Original footnote (h) becomes new footnote (g). Annual percentiles: New footnote (h): For each pollutant, report the Annual 95th percentile of hourly means in the first column and the Annual 95th percentile ELV in the second column. However, if there is an in-year reduction of the percentile ELV then it is not mandatory to enter the ELV as compliance assessment will commence in the following year. Form CON1 corrected as follows: Addition to footnote f): However, if there is an in-year reduction of the percentile ELV then it is not mandatory to enter the ELV as compliance assessment will commence in the following year.
3.1 | 2021-04-01 | Form CON2 amended as follows: Optional ammonia reporting added for processes with SCR/SNCR abatement.
3.2 | 2023-11-01 | Form CON2 amended as follows: Optional ammonia reporting added for processes with SCR/SNCR abatement.
3.3 | 2025-04-01 | Forms PM4, FUEL1 & FUEL2 removed following coal closures. Form SF6 added.
3.4 | 2025-11-01 | Forms CEM2 and CEM3 added to record CEMS calibration information for Utility Boilers and Gas Turbines.
3.5 | 2025-12-01 | Editorial correction to the List of forms (swapping titles of CEM1 and CEM2/3)

## List of forms concise
Permit | Title
IED/LCPBREF HR1 | ANNUAL OPERATING HOURS RETURN
For each LCP: Annual operating hours. For each LCP with a Limited Lifetime Derogation or a 10,000h monitoring derogation: cumulative operating hours from 1 Jan 2016. For each Unit or LCP with an IED Annex V or LCP BREF 1,500 h/yr provision: annual operating hours (from entry month in first year and 1 January in subsequent years) and five year running average from entry month. For a combined cycle gas turbine that operates with a bypass stack in normal operation, the bypass hours during normal operation are included in the plant hours but are also reported separately. Total hours of excluded emissions data, relating to forced operation in support of Black Start Events, is also recorded on this form. This is the sum of excluded hours relating to all submissions of Form LCPBREF BS1 within the reporting year or, when these emissions are aggregated within Form IED/LCPBREF MF1, a manual estimate of Black Start hours within the calendar year.
IED/LCPBREF AR1 | ANNUAL RETURN OF ENERGY INPUT AND TOTAL EMISSIONS (DELETED)
IED Article 72 Inventory: annual energy and annual mass emissions return. Annual declaration of rated thermal input. (This form is supplied annually by the Environment Agency or on request)
IED/LCPBREF CON1/2 | QUARTERLY RETURN: MONTHLY MEAN, MAXIMUM DAILY MEAN, ANNUAL MEAN AND ANNUAL PERCENTILE CONCENTRATIONS
Continuous monitoring results. Quarterly return for each LCP (noting that Unit(s) with a 1,500h provision under either the IED or the LCP BREF are regarded as a separate LCP). Validated concentration data: Monthly mean; Maximum Daily mean within month; Annual mean, for plants with an Annual ELV, and Annual 95th percentile of hourly means. Version 1 (IED/LCPBREF CON1) Utility Boilers; Version 2 (IED/LCPBREF CON2 ) Gas turbines.
IED/LCPBREF PM1 | PERIODIC MONITORING RESULTS (AS REQUIRED)
Periodic monitoring return (e.g., six monthly NOx, SO2, Dust or CO test results) or Alternative monitoring return (as agreed by the Competent Authority). Required when these species are not monitored continuously and at the frequency specified by the Permit.
IED/LCPBREF PM2 | PERIODIC MONITORING RESULTS (AS REQUIRED)
Periodic monitoring return for HCl and HF for solid fuel fired boilers, operating ≥ 500 h/y, for compliance assessment, typically quarterly or annual monitoring. Periodic monitoring return for NH3 and SO3 for plants fitted with Non-Selective or Selective Catalytic Reduction (SNCR/SCR), typically annual monitoring.
IED/LCPBREF PM3 | PERIODIC MONITORING RESULTS (AS REQUIRED)
Periodic monitoring return for trace metals, and mercury, for solid fuel fired boilers operating ≥ 500 h/y. Typically annual monitoring.
IED/LCPBREF BD1 | QUARTERLY RETURN OF CUMULATIVE ANNUAL ROLLING MALFUNCTION AND BREAKDOWN HOURS
For each LCP fitted with abatement, return the cumulative Malfunction and Breakdown hours as a rolling average (12 monthly period) that is updated on a monthly basis.
IED/LCPBREF MF1 | RETURN OF MALFUNCTION AND BREAKDOWN DATA (AS REQUIRED)
Validated concentration data for each day affected by Malfunction or Breakdown.
IED/LCPBREF BS1 | RETURN OF BLACK START DATA (AS REQUIRED)
Validated concentration data for each day affected by Black Start running.
IED/LCPBREF AQRA1 | AIR QUALITY RISK ASSESSMENT FOR OTNOC - UTILITY BOILERS (AS REQUIRED)
Basic air quality risk assessment for valid concentration excursions related to Other Than Normal Operating Conditions (Malfunction/Breakdown or Black Start running). Select pollutants from: SO2; NO2; Dust
IED/LCPBREF AQRA2 | AIR QUALITY RISK ASSESSMENT FOR OTNOC - GAS TURBINES (AS REQUIRED)
Basic air quality risk assessment for valid concentration excursions related to Other Than Normal Operating Conditions (Malfunction/Breakdown or Black Start running). Select pollutants from: NO2; CO
IED/LCPBREF CEM1 | CONTINUOUS EMISSIONS MEASUREMENT SYSTEMS (CEMS) INVALIDITY LOG
This form is submitted in the event that the CEMS unavailability exceeds 10 days in a given calendar year.
IED/LCPBREF CEM2/3 | ANNUAL RETURN OF CEMS CALIBRATION DATA
Return by the end of the quarter in which a new QAL2 calibration function is applied or an existing function is validated by an AST. CEM2 Utility Boilers; CEM3 Gas turbines.
IED/LCPBREF REM1 | ANNUAL RETURN OF RESOURCE EFFICIENCY METRICS
Energy consumption and production; water consumption and discharge; waste disposal and recovery.
IED/LCPBREF SF6 | ANNUAL RETURN OF SF6 TOP UP REPORTING
For each item of electrical equipment that has been topped up with SF6 within the calendar year. Tracks SF6 emissions and leak rates. (Replace example with own data)

## IED HR1
RELEASES TO AIR
ANNUAL RETURN
OPERATING HOURS
Operator: |  |  |  |  | Form: |  | IED/LCPBREF HR1
Location: |  |  |  |  | Vers./date: |  | V3.4 Nov 2025
Permit/Variation Number:
Year: | LCP1 (hours) | Bypass (hours) | LCP2 (hours) | Bypass (hours) | LCP3 (hours) | Bypass (hours) | LCP4 (hours) | Bypass (hours)
Annual Operating Hours (a), (b)
Cumulative Operating Hours (c),(d)
Annual Operating Hours 1,500 Unit (e) Enter start date below hours in brackets e.g., (1/7/20) or (1/8/21)
Five year rolling average (f)
Black start hours (h)
NOTES:
(a) Annual operating hours for every LCP from 1-Jan in calendar year, excluding Start-Up and Shut-down (SU-SD). (For gas turbines with a Bypass stack, include the Bypass stack operating hours, excluding SU-SD, even though these are reported separately).
(b) For gas turbines with a Bypass stack, report Bypass operating hours from 1-Jan in calendar year, excluding SU-SD, in the adjacent column (labelled Bypass) which may be deleted if not applicable.
(c) Cumulative operating hours from 1-Jan-2016 for LCP subject to a Limited Lifetime Derogation or a 10,000h monitoring derogation, excluding SU-SD. (For gas turbines with a Bypass stack, include the Bypass stack operating hours, excluding SU-SD, even though these are reported separately).
(d) For gas turbines with a Bypass stack, report Bypass Cumulative operating hours from 1-Jan-2016 if subject to a separate 10,000h monitoring derogation, in the adjacent column (labelled Bypass), excluding SU-SD.
(e) Annual operating hours in the given calendar year from the entry month into the 1,500 h/yr provision (in the first year as applicable) or from 1-Jan in subsequent calendar years, for either the whole LCP or the part of the LCP with emission limits that are applicable for <1500 h/yr operation, excluding SU-SD. For example, a plant that enters a 1,500 h/yr derogation when entering the LCP BREF compliance period would commence reporting the calendar year total hours counting from 1/8/2021.
(f) Five year rolling average hours from entry month for either the whole LCP or the part of the LCP with emission limits applicable for <1500 h/yr operation, excluding SU-SD. For example, a plant that enters a 1,500 h/yr derogation when entering the LCP BREF compliance period would commence reporting the rolling average hours from 1/8/2021.
(g) General note: hours of normal operation, excluding SU-SD, are reported as a decimal number to two decimal places.
(h) Hours of excluded emissions data associated with Black Start running (total excluded hours from all in-year submissions of Form IED/LCPBREF BS1 or a manual estimate if only Form MF1 is used to report Total OTNOC).
Signed on behalf of the Operator by: | ……………..……………………………………..
Date of return: | ……………..……………………………………..

## IED CON1
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN, ANNUAL MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
Operator: | [6 empty] | Form: | IED/LCPBREF CON1 (Utility boilers)
Location: | [6 empty] | Vers./date: | V3.4 Nov 2025
Permit/Variation Number:
Year: LCP: | SO2 (mg/m3) |  | NOx (mg/m3) |  | Dust (mg/m3) |  | CO (mg/m3) |  | HCl (mg/m3)(g) |  | NH3 (mg/m3)(h)
Month | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean | Monthly Mean | Max Daily Mean
January
February
March
April
May
June
July
August
September
October
November
December
Monthly ELV & Daily ELV: (Period 1)(d)
Monthly ELV & Daily ELV: (Period 2)(d)
| Annual Mean | Annual ELV | Annual Mean | Annual ELV | Annual Mean | Annual ELV | Annual Mean | Annual ELV | Annual Mean | Annual ELV | Annual Mean | Annual ELV
Annual Mean & ELV (e)
| Annual Percentile | Percentile ELV | Annual Percentile | Percentile ELV | Annual Percentile | Percentile ELV | Annual Percentile | Percentile ELV | Annual Percentile | Percentile ELV | Annual Percentile | Percentile ELV
Annual 95th Percentile & ELV (f)
NOTES:
(a) All concentration data are based on validated hourly mean concentrations excluding start-up and shut-down, periods of Malfunction or Breakdown of abatement equipment or Black Start operation. Repeat the report for each LCP as required.
(b) Daily, Monthly and Annual means, and Annual percentile concentrations, are calculated from the validated hourly means defined in (a). The qualifying periods for Hourly, Daily, Monthly and Annual means are 40m, 6h, 72h or 3d, and 500h, respectively. Annual means, for plants with an Annual ELV, and Annual Percentile concentrations, are submitted with the final return (Quarter 4).
(c) Reference conditions. Solid fuel: 6% O2 (dry) Liquid fuel: 3% O2 (dry) at 273.15K, 101.3 kPa.
(d) When there is an in-year change of ELV, record both ELVs in consecutive rows. For example, compliance with the LCP BREF begins in August 2021 therefore replace 'Period 1' with 'Jan - Jul' and 'Period 2' with 'Aug - Dec'. Otherwise, replace 'Period 1' with 'Jan - Dec' and delete or blank out the row containing 'Period 2'.
(e) For plants with an Annual ELV, for each pollutant, report the Annual mean in the first column and the Annual ELV in the second column. Annual ELVs are not applicable, and are not entered on the form, when the plant operates less than 1500 hours within the reporting year or for plant with a 1500 h/yr five-year rolling average provision. Otherwise, reporting of the Annual mean begins in 2021 but compliance assessment with the Annual ELV begins in 2022 (incorporating plant operation from 1 January 2022); the Annual ELV is therefore not entered on the form for 2021 reporting.
(f) For each pollutant, report the Annual 95th percentile of hourly means in the first column and the Annual 95th percentile ELV in the second column. However, if there is an in-year reduction of the percentile ELV then it is not mandatory to enter the ELV as compliance assessment will commence in the following year. Delete columns containing pollutants that are not applicable to the plant type.
(g) Continuous HCl monitoring is always required for boilers fired by solid biomass (> 100 MWth), unless the emissions are recognised as being 'sufficiently stable' by the Competent Authority (delete columns if not required). Monthly and Annual Percentile ELVs are not specified since HCl was not regulated previously under the IED.
(h) Continuous NH3 monitoring is required for processes fitted with Selective Catalytic Reduction (SCR) or Non-Selective Catalytic Reduction (SNCR) (delete columns if not required). In the case of SCR only, continuous monitoring is not required if the emissions are recognised as being 'sufficiently stable' by the Competent Authority. Only an Annual ELV is specified.
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## IED CON2
RELEASES TO AIR
QUARTERLY RETURN
MONTHLY MEAN, MAXIMUM DAILY MEAN, ANNUAL MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE:
Operator: |  |  |  |  | Form: | IED/LCPBREF CON2 (Gas Turbines)
Location: |  |  |  |  | Vers./date: | V3.4 Nov 2025
Permit/Variation Number:
Year: | LCP:
| NOx (mg/m3) |  |  | CO (mg/m3) |  |  | NH3 (mg/m3)(i)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January
February
March
April
May
June
July
August
September
October
November
December
Monthly ELV & Daily ELVs: (Period 1)(f)
Monthly ELV & Daily ELVs: (Period 2)(f)
| Annual Mean (d) | Annual ELV |  | Annual Mean (d) | Annual ELV |  | Annual Mean (d) | Annual ELV
Annual Mean & ELV (g)
| Annual Percentile (d) | Annual ELV |  | Annual Percentile (d) | Annual ELV |  | Annual Percentile (d) | Annual ELV
Annual 95th Percentile & ELV (h)
NOTES:
(a) All concentration data, at 15% O2, dry, 273.15K, 101.3 kPa, are based on validated hourly mean concentrations, excluding start-up and shut-down, periods of Malfunction or Breakdown of abatement equipment or Black Start operation.
(b) Daily, Monthly and Annual means, and Annual percentile concentrations, are calculated from the validated hourly means defined in (a). CCGT qualifying periods for Hourly, Daily, Monthly and Annual averages are 40m, 6h, 72h or 3d, and 500h, respectively. OCGT qualifying periods are the same apart from the Hourly qualifying period which is reduced to 20m of normal operation. Annual averages, for plants with an Annual ELV, and Annual percentile concentrations, are submitted with the final return (Quarter 4).
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing.
(d) Averages determined at loads in the range E-DLN < Load ≤ 100% ISO base load and above (where E-DLN is the Effective-DLN load point).
(e) Averages determined in the range MSUL* < Load ≤ 100% ISO base load and above. (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down).
(f) When there is an in-year change of ELV, record both ELVs in consecutive rows. For example, compliance with the LCP BREF begins in August 2021 therefore replace 'Period 1' with 'Jan - Jul' and 'Period 2' with 'Aug - Dec'. Otherwise, replace 'Period 1' with 'Jan - Dec' and delete or blank out the row containing 'Period 2'.
(g) For plants with an Annual ELV, for each pollutant, report the Annual mean in the first column and the Annual ELV in the second column. Annual ELVs are not applicable, and are not entered on the form, when the plant operates less than 1500 hours within the reporting year or for plant with a 1500 h/yr five-year rolling average derogation. Otherwise, reporting of the Annual mean begins in 2021 but compliance assessment with the Annual ELV begins in 2022 (incorporating plant operation from 1 January 2022); the Annual ELV is therefore not entered on the form for 2021 reporting.
(h) For each pollutant, report the Annual 95th percentile of hourly means in the first column and the Annual 95th percentile ELV in the second column. However, if there is an in-year reduction of the percentile ELV then it is not mandatory to enter the ELV as compliance assessment will commence in the following year.
(i) Continuous NH3 monitoring is required for processes fitted with Selective Catalytic Reduction (SCR) or Non-Selective Catalytic Reduction (SNCR) (delete columns if not required). In the case of SCR only, continuous monitoring is not required if the emissions are recognised as being 'sufficiently stable' by the Competent Authority. Only an Annual ELV is specified.
Signed on behalf of the Operator by: |  |  | ……………..………………………………………
Date of return: |  |  | ……………..………………………………………

## IED PM1
RELEASES TO AIR
RETURN OF PERIODIC MONITORING RESULTS(a)
Operator:
Location: |  |  | Form: IED/LCPBREF PM1
Permit/Variation Number: |  |  | V3.4 Nov 2025
Year: | LCP:
Period:(b)
Measurement details | NOx (mg/m3) | SO2 (mg/m3) | Dust (mg/m3) | CO (mg/m3)
Date(s)
Measurement 1 (c) (Duration in HH:MM)
Measurement 2 (c) (Duration in HH:MM)
Measurement 3 (c) (Duration in HH:MM)
Average result
Measurement Uncertainty(d)
Operational data(e)
Load (%MCR)
Fuel 1 name (%)
Fuel 2 name (%)
Fuel 3 name (%)
Alternative approach (f), (g)
Method
Result
Emission Limit Value
NOTES:
(a) Periodic monitoring when continuous monitoring is not required. Reference conditions for mg/m3 are 15% O2 CCGT, 6% O2 solid fuels, 3% O2 for oil and gas, dry, 273.15K, 101.3 kPa.
(b) Period, e.g., Jan - Mar for Quarterly, Jan - Jun for Six-Monthly or Jan - Dec for Annual.
(c) Enter the measurement result followed by the sampling duration in parentheses, e.g., 50.5 (1:05).
(d) Expanded measurement uncertainty (95% confidence) declared by the Test Laboratory in concentration units. The maximum allowed uncertainty for compliance assessment is specified by the competent authority.
(e) Operational data for the test period. Declare fuel split if another fuel is co-fired. (MCR = Maximum Continuous Rating)
(f) Alternative approach to periodic monitoring by agreement with the Competent Authority.
(g) Use abbreviation for Method: NF for agreed NOx factor, FS for fuel sulphur content, CS for agreed CO factor, DF for agreed dust factor. The flue gas concentration calculated using this method is the Result.
Signed on behalf of the Operator by: ………………………………………
Date of return: ………………………………………

## IED PM2
RELEASES TO AIR
RETURN OF PERIODIC MONITORING RESULTS (a), (b)
Operator:
Location: |  |  | Form: IED/LCPBREF PM2
Permit/Variation Number: |  |  | V3.4 Nov 2025
Year: | LCP:
Period:(c)
Measurement details | HCl (mg/m3) | HF (mg/m3) | NH3(e) (mg/m3) | SO3(e) (mg/m3)
Date(s)
Measurement 1(d) (Duration in HH:MM)
Measurement 2(d) (Duration in HH:MM)
Measurement 3(d) (Duration in HH:MM)
Average result (mg/m3)
Measurement Uncertainty (mg/m3)(f)
Annual ELV (mg/m3)
Operational data(g)
Load (%MCR)
Fuel 1 name (%)
Fuel 2 name (%)
Fuel 3 name (%)
NOTES:
(a) Periodic monitoring at the frequency required by the Permit. For coal fired plants only, and for HCl and HF only, for operation < 500h/y, use Form IED/LCPBREF FUEL2 instead.
(b) Reference conditions for reporting concentrations: 6% O2, dry, 273.15K, 101.3 kPa.
(c) Period, e.g., Jan - Mar for Quarterly, Jan - Jun for Six-Monthly or Jan - Dec for Annual.
(d) Enter the measurement result followed by the sampling duration in parentheses, e.g., 5.52 (1:33)
(e) For processes fitted with Selective Catalytic Reduction (SCR) only. Annual monitoring of SO3. Annual monitoring of NH3 if the emissions are recognised as being 'sufficiently stable' by the Competent Authority. Delete columns if not required.
(f) Average Expanded measurement uncertainty (95% confidence) reported by the Test Laboratory. The maximum allowed uncertainty for compliance assessment is specified by the competent authority.
(g) Operational data for the test period. Declare Load as % of MCR (Maximum Continuous Rating). Declare fuel split when mixed fuels are fired.
Signed on behalf of the Operator by: ………………………………………
Date of return: ………………………………………

## IED PM3
RELEASES TO AIR
RETURN OF PERIODIC MONITORING RESULTS (a), (b)
Operator:
Location: | [13 empty] | Form: IED/LCPBREF PM3
Permit/Variation Number: | [13 empty] | V3.4 Nov 2025
Year: | LCP:
Period:(c)
Units | (mg/m3) | [13 empty] | (mg/m3)
Measurements | As | Cd | Co | Cr | Cu | Mn | Ni | Pb | Sb | Se | Tl | V | Zn | Measurements | Hg
Date(s) | [13 empty] | Date(s)
Average Duration (HH:MM) | [13 empty] | Average Duration (HH:MM)
Measurement 1 | [13 empty] | Measurement 1
Measurement 2 | [13 empty] | Measurement 2
Measurement 3 | [13 empty] | Measurement 3
Average result (mg/m3) | [13 empty] | Average result (mg/m3)
Uncertainty (mg/m3)(d) | [13 empty] | Uncertainty (mg/m3)(d)
Annual ELV (mg/m3) | [13 empty] | Annual ELV (mg/m3)
Operational data(e) | [13 empty] | Operational data(e)
Load (%MCR) | [13 empty] | Load (%MCR)
Fuel 1 name (%) | [13 empty] | Fuel 1 name (%)
Fuel 2 name (%) | [13 empty] | Fuel 2 name (%)
Fuel 3 name (%) | [13 empty] | Fuel 3 name (%)
NOTES:
(a) Periodic monitoring at the frequency required by the Permit. For coal fired plants subject to 'sufficiently stable' emissions criteria, mercury (Hg) is reported instead on Form IED/LCPBREF PM4.
(b) Reference conditions for reporting concentrations: 6% O2, dry, 273.15K, 101.3 kPa.
(c) Period, e.g., Jan - Mar for Quarterly, Jan - Jun for Six-Monthly or Jan - Dec for Annual.
(d) Average Expanded measurement uncertainty (95% confidence) reported by the Test Laboratory. The maximum allowed uncertainty for compliance assessment is specified by the competent authority.
(e) Operational data for the test period. Declare Load as % of MCR (Maximum Continuous Rating). Declare fuel split when mixed fuels are fired.
Signed on behalf of the Operator by: ………………………………………
Date of return: ………………………………………

## IED BD1
RELEASES TO AIR
QUARTERLY RETURN
CUMULATIVE ROLLING MALFUNCTION AND BREAKDOWN HOURS (12 MONTH PERIOD)(a), (b)
Operator: | [7 empty] | Form: | IED/LCPBREF BD1
Location: | [7 empty] | Vers./date: | V3.4 Nov 2025
Permit/Variation Number:
Year: LCP: | SO2 |  | NOx |  | Dust |  | CO(d) |  | HCl(e)
Month(c) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours) | Malfunction (hours) | Breakdown (hours)
Month 1
Month 2
Month 3
Month 4
Month 5
Month 6
Month 7
Month 8
Month 9
Month 10
Month 11
Month 12
Annual cap (hours) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
NOTES:
(a) Cumulative rolling malfunction and breakdown hours (12 month period) updated monthly
(b) Data Acquisition and Handling Systems without the capability to report Black Start hours separately may incorporate Black Start hours on this form provided that a manual estimate of the number of Black Start hours is reported separately on Form IED/LCPBREF HR1.
(c) Insert the relevant months for the preceding 12 month period, e.g., starting with March 2016
(d) Gas turbines with CO abatement only (columns may be deleted for other plant types)
(e) Plants with HCl abatement only (columns may be deleted for other plant types) | (f) Plants with HCl abatement only (columns may be deleted for other plant types)
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## IED MF1
RELEASES TO AIR
RETURN OF DAILY MALFUNCTION AND BREAKDOWN DATA (a), (b), (c), (d)
Operator:
Location: | [8 empty] | Form: | IED/LCPBREF MF1
Permit/Variation Number: | [8 empty] | Vers/date: | V3.4 Nov 2025
LCP:
Type: | Malfunction/Breakdown /Normal Operation
Date: |  | SO2 | Excluded? | NOx | Excluded? | Dust | Excluded? | CO (e) | Excluded? | HCl (f) | Excluded?
Hour | Start time | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N
1 | 0:00
2 | 1:00
3 | 2:00
4 | 3:00
5 | 4:00
6 | 5:00
7 | 6:00
8 | 7:00
9 | 8:00
10 | 9:00
11 | 10:00
12 | 11:00
13 | 12:00
14 | 13:00
15 | 14:00
16 | 15:00
17 | 16:00
18 | 17:00
19 | 18:00
20 | 19:00
21 | 20:00
22 | 21:00
23 | 22:00
24 | 23:00
| Daily | Average | No. Hours | Average | No. Hours | Average | No. Hours | Average | No. Hours | Average | No. Hours
Without data exclusion (All of the above data)
With data exclusion (Reportable data only)
Notes: | (a) Produce a return for each day which has data exclusion due to Malfunction or Breakdown
(b) All data based on hourly average validated concentrations (confidence interval subtracted)
(c) Reference conditions: mg/m3 dry, 273.15K, 101.3 kPa; Solid fuels 6% O2; Liquid and Gaseous fuels 3% O2; Gas turbines 15% O2
(d) Data Acquisition and Handling Systems without the capability to report Black Start emissions separately may incorporate Black Start emissions on this form provided that a manual estimate of the number of Black Start hours is reported separately on Form IED/LCPBREF HR1.
(e) Gas turbines with abatement only (columns may be deleted for other plant types)
(f) Plants with HCl abatement only (columns may be deleted for other plant types)
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## IED BS1
RELEASES TO AIR
RETURN OF DAILY BLACK START DATA (a), (b), (c), (d)
Operator:
Location: | [7 empty] | Form: | IED/LCPBREF BS1
Permit/Variation Number: | [7 empty] | Vers/date: | V3.4 Nov 2025
LCP:
Type: | Black Start /Normal Operation
Date: |  | SO2 | Excluded? | NOx | Excluded? | Dust | Excluded? | CO (e) | Excluded? | HCl (f) | Excluded?
Hour | Start time | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N | mg/m3 | Y/N
1 | 0:00
2 | 1:00
3 | 2:00
4 | 3:00
5 | 4:00
6 | 5:00
7 | 6:00
8 | 7:00
9 | 8:00
10 | 9:00
11 | 10:00
12 | 11:00
13 | 12:00
14 | 13:00
15 | 14:00
16 | 15:00
17 | 16:00
18 | 17:00
19 | 18:00
20 | 19:00
21 | 20:00
22 | 21:00
23 | 22:00
24 | 23:00
| Daily | Average | No. Hours | Average | No. Hours | Average | No. Hours | Average | No. Hours | Average | No. Hours
Without data exclusion (All of the above data)
With data exclusion (Reportable data only)
Notes: | (a) Produce a return for each day which has data exclusion due to Black Start running
(b) All data based on hourly average validated concentrations (confidence interval subtracted)
(c) Reference conditions: mg/m3 dry, 273.15K, 101.3 kPa; Solid fuels 6% O2; Liquid and Gaseous fuels 3% O2; Gas turbines 15% O2
(d) Data Acquisition and Handling Systems without the capability to report Black Start emissions separately may incorporate Black Start emissions on form IED/LCPBREF MF1 provided that a manual estimate of the number of Black Start hours is reported separately on Form IED/LCPBREF HR1.
(e) As applicable, e.g., gas turbines
(f) Plants with HCl abatement only (columns may be deleted for other plant types)
Signed on behalf of the Operator by: |  |  | ……………..………………………………………………..
Date of return: |  |  | ……………..………………………………………………..

## IED AQRA1
Air Quality Risk Assessment | Form: IED/LCPBREF AQRA1 Utility Boilers (V3.4 Nov 2025)
Operator:
Contact:
Location:
Permit number:
Pollutant(s) (SO2, NOx, Dust):
Sulphur Dioxide (SO2) | SO2
First excluded hour (DD-MM-YYYY HH:MM):
Last excluded hour (DD-MM-YYYY HH:MM):
Notification period commenced (DD-MM-YYYY 00:00):
Number of excluded hours
Maximum hourly average valid concentration (mg/m3):
Maximum daily average valid concentration (mg/m3):
Daily Emission Limit Value (mg/m3):
Number of running units:
Local Air Quality Assessment: Note any relevant observations from local air quality monitoring stations and comment on weather conditions, including prevailing wind speed (maximum and average) and direction.
Dispersion Assessment: Comment on the magnitude of the maximum hourly average concentration in relation to previous dispersion modelling studies.
Further dispersion modelling required (Y/N)?
Nitrogen Oxides (NOx as NO2) | NO2
First excluded hour (DD-MM-YYYY HH:MM):
Last excluded hour (DD-MM-YYYY HH:MM):
Notification period commenced (DD-MM-YYYY 00:00):
Number of excluded hours
Maximum hourly average valid concentration (mg/m3):
Maximum daily average valid concentration (mg/m3):
Daily Emission Limit Value (mg/m3):
Number of running units:
Local Air Quality Assessment: Note any relevant observations from local air quality monitoring stations and comment on weather conditions, including prevailing wind speed (maximum and average) and direction.
Dispersion Assessment: Comment on the magnitude of the maximum hourly average concentration in relation to previous dispersion modelling studies.
Further dispersion modelling required (Y/N)?
DUST (as PM10) | PM10
First excluded hour (DD-MM-YYYY HH:MM):
Last excluded hour (DD-MM-YYYY HH:MM):
Notification period commenced (DD-MM-YYYY 00:00):
Number of excluded hours
Maximum hourly average valid concentration (mg/m3):
Maximum daily average valid concentration (mg/m3):
Daily Emission Limit Value (mg/m3):
Number of running units:
Local Air Quality Assessment: Note any relevant observations from local air quality monitoring stations and comment on weather conditions, including prevailing wind speed (maximum and average) and direction.
Dispersion Assessment: Comment on the magnitude of the maximum hourly average concentration in relation to previous dispersion modelling studies.
Further dispersion modelling required (Y/N)?
Notes:
Reference condition: mg/m3 at 6% O2, dry, 273.15K, 101.3 kPa.
Valid Concentration Averages incorporate previously excluded data.
Air quality objectives are set for SO2 (15min, Hourly, Daily averages); NO2 (Hourly) and PM10 (Daily).

## IED AQRA2
Air Quality Risk Assessment | Form: IED/LCPBREF AQRA2 Gas turbines (V3.4 Nov 2025)
Operator:
Contact:
Location:
Permit number:
Pollutant(s) considered (NOx, CO):
Nitrogen Oxides (NOx as NO2) | NO2
First excluded hour (DD-MM-YYYY HH:MM):
Last excluded hour (DD-MM-YYYY HH:MM):
Notification period commenced (DD-MM-YYYY 00:00):
Number of excluded hours
Maximum hourly average valid concentration (mg/m3):
Maximum daily average valid concentration (mg/m3):
Daily Emission Limit Value (mg/m3):
Number of running units:
Local Air Quality Assessment: Note any relevant observations from local air quality monitoring stations and comment on weather conditions, including prevailing wind speed (maximum and average) and direction.
Dispersion Assessment: Comment on the magnitude of the maximum hourly average concentration in relation to previous dispersion modelling studies.
Further dispersion modelling required (Y/N)?
Carbon monoxide (CO) | CO
First excluded hour (DD-MM-YYYY HH:MM):
Last excluded hour (DD-MM-YYYY HH:MM):
Notification period commenced (DD-MM-YYYY 00:00):
Number of excluded hours
Maximum hourly average valid concentration (mg/m3):
Maximum daily average valid concentration (mg/m3):
Daily Emission Limit Value (mg/m3):
Number of running units:
Local Air Quality Assessment: Note any relevant observations from local air quality monitoring stations and comment on weather conditions, including prevailing wind speed (maximum and average) and direction.
Dispersion Assessment: Comment on the magnitude of the maximum hourly average concentration in relation to previous dispersion modelling studies.
Further dispersion modelling required (Y/N)?
Notes:
Reference condition: mg/m3 at 15% O2, dry, 273.15K, 101.3 kPa.
Valid Concentration Averages incorporate previously excluded data.
Air quality objectives are set for: NO2 (Hourly average); CO (8h running average).

## IED CEM1
RELEASES TO AIR
ANNUAL RETURN
CONTINUOUS EMISSIONS MEASUREMENT SYSTEMS (CEMS) INVALIDITY LOG(a),(b)
Operator: |  |  |  | Form: IED/LCPBREF CEM1
Monitor positioned on release point/LCP Number: |  |  |  | V3.4 Nov 2025
Permit/Variation Number:
LCP:
Year: | Period of Invalidation (hours) | Cumulative Invalidated Days in a Year | Comments
Date
NOTES:
(a) This form is returned in the event that the number of days of invalid CEMS performance exceeds 10 days within the calendar year for any individual pollutant.
(b Any day in which more than 3 hourly average values are invalid (due to malfunction or maintenance of the CEMS) is counted as a day of CEMS invalidity. If more than 10 days are invalid over a year the operator shall, within 28 days of becoming aware of this fact, review the causes of the invalidity and submit to the Environment Agency for approval, proposals for measures to improve the reliability of the CEMS, including a timetable for the implementation of those measures, and then implement the approved proposals.
Signed on behalf of the Operator by: |  | ……………..……………………………………..
Date of return: |  | ……………..……………………………………..

## IED CEM2
RELEASES TO AIR
ANNUAL RETURN (a)
CEMS CALIBRATION DATA
Operator: |  | Form: |  | IED/LCPBREF CEM2 (Utility boilers)
Location: |  | Vers./date: |  | V3.4 Nov 2025
Permit/Variation Number:
Calibration information for continuously monitored pollutants (b) |  |  | CEMS ID: |  |  |  | Reference Parameters
Year: LCP: | NOx | CO | SO2 | HCl | NH3 | Dust | O2 | H2O | Flow (j)
Date(s) of existing QAL2 test (c)
Existing Calibration Function gradient 'b' value (d)
Existing Calibration Function offset 'a' value (d)
Date of Annual Surveillance Test (AST) (e)
Variability Test Passed (Y/N)
Calibration Validity Test Passed (Y/N)
Description of actions to investigate AST failure(s) prior to new QAL2 being undertaken (f)
Date(s) of new QAL2 test (g)
Date of new QAL2 report (h)
New Calibration Function gradient 'b' value (d)
New Calibration Function offset 'a' value (d)
Date new Calibration Function entered on Data Acquisition and Handling System (d)(i)
NOTES:
(a) Return the form at the end of the the quarter in which a new QAL2 calibration function is applied or an existing function is validated by an AST. In both cases, the function must be applied or validated within six weeks of receiving the test laboratory report and, in all cases, no later than six months from the test date.
(b) Repeat this table if there are multiple CEMS serving the LCP.
(c) Test date. If this is the first QAL2, leave this existing (current) QAL2 section blank and fill in the new QAL2 section below. Enter 'First QAL2' in the 'Description of actions'.
(d) Calibration Function: y = bx + a
(e) If a repeat QAL2 is scheduled instead of an AST, leave this section blank and fill in the new QAL2 section. Enter 'Repeat QAL2 due' in the 'Description of actions'.
(f) When the CEMS pass the AST, leave the following QAL2 section blank unless an elective QAL2 is conducted as an extension of the AST. In the event of an AST fail, enter a description of actions to investigate and rectify the failure, and enter the new QAL2 details below.
(g) Test date. New QAL2 test date (no later than six months from the test date of of a failed AST).
(h) Publication date of finalised test laboratory report.
(i) Implement the QAL2 function within 6 weeks of the receipt of the published final QAL2 report and no later than 6 months after the date of the QAL2 test.
(j) When the CEMS is a flow calculation, the QAL2/AST is used to verify the calculated flow rate. Fill in the AST validity test result for both a QAL2 or an AST but do not enter QAL2 factors as a calibration is not applied. If additional QA is applied to the calculation inputs, such that an AST is not required, then enter 'Flow AST not required' in the 'Description of actions'.
Signed on behalf of the Operator by: |  | ……………..…………………………………………………...........
Date of return: |  | ……………..…………………………………………………...........

## IED CEM3
RELEASES TO AIR
ANNUAL RETURN (a)
CEMS CALIBRATION DATA
Operator: | Form: |  | IED/LCPBREF CEM3 (GT)
Location: | Vers./date: |  | V3.4 Nov 2025
Permit/Variation Number:
Calibration information for continuously monitored pollutants (b) |  | CEMS ID: |  | Reference Parameters
Year: LCP: | NOx | CO | NH3 | O2 | H2O | Flow (j)
Date(s) of existing QAL2 test (c)
Existing Calibration Function gradient 'b' value (d)
Existing Calibration Function offset 'a' value (d)
Date of Annual Surveillance Test (AST) (e)
Variability Test Passed (Y/N)
Calibration Validity Test Passed (Y/N)
Description of actions to investigate AST failure(s) prior to new QAL2 being undertaken (f)
Date(s) of new QAL2 test (g)
Date of new QAL2 report (h)
New Calibration Function gradient 'b' value (d)
New Calibration Function offset 'a' value (d)
Date new Calibration Function entered on Data Acquisition and Handling System (d)(i)
NOTES:
(a) Return the form at the end of the the quarter in which a new QAL2 calibration function is applied or an existing function is validated by an AST. In both cases, the function must be applied or validated within six weeks of receiving the test laboratory report and, in all cases, no later than six months from the test date.
(b) Repeat this table if there are multiple CEMS serving the LCP.
(c) Test date. If this is the first QAL2, leave this existing (current) QAL2 section blank and fill in the new QAL2 section below. Enter 'First QAL2' in the 'Description of actions'.
(d) Calibration Function: y = bx + a
(e) If a repeat QAL2 is scheduled instead of an AST, leave this section blank and fill in the new QAL2 section. Enter 'Repeat QAL2 due' in the 'Description of actions'.
(f) When the CEMS pass the AST, leave the following QAL2 section blank unless an elective QAL2 is conducted as an extension of the AST. In the event of an AST fail, enter a description of actions to investigate and rectify the failure, and enter the new QAL2 details below.
(g) Test date. New QAL2 test date (no later than six months from the test date of of a failed AST).
(h) Publication date of finalised test laboratory report.
(i) Implement the QAL2 function within 6 weeks of the receipt of the published final QAL2 report and no later than 6 months after the date of the QAL2 test.
(j) When the CEMS is a flow calculation, the QAL2/AST is used to verify the calculated flow rate. Fill in the AST validity test result for both a QAL2 or an AST but do not enter QAL2 factors as a calibration is not applied. If additional QA is applied to the calculation inputs, such that an AST is not required, then enter 'Flow AST not required' in the 'Description of actions'.
Signed on behalf of the Operator by: | ……………..……………………………………………
Date of return: | ……………..……………………………………………

## IED REM1
RESOURCE EFFICIENCY METRICS
ANNUAL RETURN YEAR:
Form: IED/LCPBREF REM1 Vers./date: | V3.4 Nov 2025
Operator:
Permit/Variation Number:
Parameter | (a) | Units
Electricity Exported |  | GWh
Heat Exported |  | GWh
Mechanical Power Provided |  | GWh
Fossil Fuel Energy Consumption |  | GWh
Non-Fossil Fuel Consumption |  | GWh
Annual Operating Hours - LCPXXX(b) |  | h
Water Abstracted from Fresh Water Source |  | m3
Water Abstracted from Borehole Source |  | m3
Water Abstracted from Estuarine Water Source |  | m3
Water Abstracted from Sea Water Source |  | m3
Water Abstracted from Mains Water Source |  | m3
Gross Total Water Used |  | m3
Net Water Used |  | m3
Hazardous Waste Transferred for Disposal at another Installation |  | t
Hazardous Waste Transferred for Recovery at another Installation |  | t
Non-Hazardous Waste Transferred for Disposal at another Installation |  | t
Non-Hazardous Waste Transferred for Recovery at another Installation |  | t
Waste Recovered to Quality Protocol Specification and Transferred Off-Site |  | t
Waste Transferred Directly Off-Site for Use under an exemption / position statement |  | t
NOTES:
(a) General note: Parameters should be reported as a decimal number to 2 decimal places.
(b) Repeat row for each LCP
Signed on behalf of the Operator by: …............................................ | ……………..……………………
Date of return: ................................................. | ……………..……………………

## IED SF6
RELEASES TO AIR
ANNUAL RETURN
SF6 TOP-UP REPORTING (a)
Operator: |  |  |  | Form: | IED/LCPBREF SF6
Location: |  |  |  | Vers./date: | V3.4 Nov 2025
Permit/Variation Number:
Plant Item | Top-up # | SF6 Inventory (kg) | Specific Annual Loss Rate (%) | Average Annual Loss Rate (%) | Leak Event (Y/N) | Schedule 5 Notification (Y/N)
Plant Item
SF6 Inventory (kg) | 500
Manufacturer's Loss Rate (%) | 0.75%
Latest Date SF6 Added (b) | 1 | 2023-07-01 | 0.6% | 0.6% | N | N
SF6 Added (kg)* |  | 0.5
Previous Date SF6 Added (c) | 2 | 2023-05-01 | 3.12% | 1.44% | Y | N
SF6 Added (kg) |  | 1.3
Date SF6 Added | 3 | 2023-04-01 | 0.07636% | 0.24% | N | N
SF6 Added (kg) |  | 0.7
Date SF6 Added | 4 | 2021-06-01 |  |  |  | N
SF6 Added (kg) |  | 0.7
Date SF6 Added | 5
SF6 Added (kg)
Date SF6 Added | 6
SF6 Added (kg)
Date SF6 Added | 7
SF6 Added (kg)
Date SF6 Added | 8
SF6 Added (kg)
Date SF6 Added | 9
SF6 Added (kg)
Date SF6 Added | 10
SF6 Added (kg)
NOTES:
(a) Year-to-date reporting of SF6 electrical switch-gear top-ups. Only report a Plant Item if there has been a top-up in the current year.
(b) Latest in-year top-up. Report all in-year top-ups in sequence below.
(c) Always report at least one previous top-up even if this is in an earlier year.
Signed on behalf of the Operator by: |  |  |  | ……………..……………………………
Date of return: |  |  |  | ……………..……………………………